Faculty of Engineering, Architecture and Science

Department of Mechanical, Industrial, and Mechatronics Engineering

| Program | Electrical Engineering |
| --- | --- |
| Course Number | ELE637 |
| Course Title | Energy Conversion |
| Semester/Year | W2025 |
| Instructor | Dr. Richard Cheung |

| Lab/Tutorial Report NO. | 1 |
| --- | --- |

| Report Title | Polyphase Power Measurement |
| --- | --- |

| Section No. | 04 |
| --- | --- |
| Submission Date | January 26, 2025 |
| Due Date | January 27, 2025 |

| Name | Student ID | Signature* |
| --- | --- | --- |
| Kyle Chin | 501118291 |  |
| Shai Mourad | 501170415 |  |

*By signing above you attest that you have contributed to this submission and confirm that all

work you have contributed to this submission is your own work. Any suspicion of copying or

plagiarism in this work will result in an investigation of Academic Misconduct and may result

in a “0” on the work, an “F” in the course, or possibly more severe penalties, as well as a

Disciplinary Notice on your academic record under the Student Code of Academic Conduct,

which can be found online at:

https://www.torontomu.ca/senate/policies/pol60.pdf.

Objectives

The objectives of this experiment are to understand the principle of operation of the two-wattmeter method, explore various methods of power measurement in electric circuits, and apply the two-wattmeter method to measure power in both balanced and unbalanced three-phase circuits.

In-Lab Results

Table 2 Measurement results for single-phase loads

| Voltage V | R Ω | C μF | Current A | Real Power W | Reactive Power VAR |
| --- | --- | --- | --- | --- | --- |
| 69.3 | 20 | 47 | 1.18 | 26.4 | -81.774 |
| 69.3 | 40 | 47 | 1.01 | 39.4 | -69.993 |

Table 3 measurement results for 3-phase balanced loads

| Load Case | Line Voltage V | R Ω/ph | C μF/ph | Phase Voltage V | Line Current A | W1 W | W2 W | W3phase W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 120 | 40 | None | 118 | 3.06 | 300 | 300 | 600 |
| 2 | 120 | None | 15 | 69.6 | 0.421 | 20 | -25 | -5 |
| 3 | 120 | 20 | 15 | 69.7 | 0.411 | 20 | -10 | 10 |
| 4 | 120 | 40 | 15 | 69.8 | 0.402 | 25 | -10 | 15 |

Table 4 Measurement results for 3-phase unbalanced loads

| Phase Voltages |  |  | Line Currents |  |  | 3-Phase Power |  | Per-Phase Powers (W3) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Volts |  |  | Amperes |  |  | Watts |  | Watts |  |  |
| An | Bn | Cn | A | B | C | W1 | W2 | A | B | C |
| 44.9 | 84.9 | 134 | 1.14 | 0.504 | 0.782 | 115 | -50 | 65 | 65 | 65 |
| VRB=8.4V, VCB=71.4V, VnN=0.045V |  |  |  |  |  |  |  |  |  |  |

Answers to In-Lab Questions

Q1. Are all of the phase-neutral voltages the same?

Yes, they are the same because nothing is connected yet therefore the system is balanced.

Q2. What is the ratio between the rms values of line voltage and phase voltage?

The ratio depends on the type of connection between the 3-phase circuit. For a Y connection, the ratio is VLVP=3. For a Δ connection, the ratio is VLVP=1.

Q3. Are the measured values of current and power the same as the corresponding calculated values in section 8 of the pre-lab part for the same circuit? Comment on possible reasons if there are any discrepancies.

The measured values of current and power are similar to the values calculated during the pre-lab. Possible reasons for discrepancies include equipment tolerance variation and measurement approximation errors.

Q4. You should expect equal positive readings on both wattmeters W1 and W2. Explain possible reasons if you do not get such a result.

Possible reasons for a result other than equal positive readings on both wattmeters include unbalanced loads, measurement errors with the wattmeters themselves, and equipment failure.

Q5. Do you expect any voltage between the neutral points of the load and the neutral point of the voltage source when the load is balanced?

No, when the load is balanced there should be no voltage between the neutral points. This is because the sum of the phase currents should be equal to zero, thus zero current flows between the neutral points of the load and the source, and there is no voltage difference between them.

Q6. Is this voltage the same as you expect? Comment on the possible reasons if your expectation is not met.

Yes, since the load is balanced, there is no voltage difference between the neutral point of the load and the neutral point of the voltage source.

Post-Lab Questions

- Summarize your recorded measurement results for three-phase balanced load cases in Table 5. Also calculate the theoretical values of power the same load cases and record your results in corresponding cells of the same table.

Table 5 Comparison of measurement and calculation results for balanced loads

| Load case | Total Power |  |  | Error |  |
| --- | --- | --- | --- | --- | --- |
|  | Measured |  | Calculated | Error of P1 | Error of P2 |
|  | P1=W1+W2 | P2=3W3 | P3=3VLILcosφ | P3-P1P3×100% | P3-P2P3×100% |
| 1 | 300W + 300W = 600W | 3*600W = 1800W | 3*120V*3.06A*1 = 636.00W | 636.00W - 600W636.00W*100 = 5.66% | 636.00W - 1800W636.00W*100 = -183.02% |
| 2 | 20W + (-25W) = -5W | 3*-5W = -15W | 3*120V*421x10-3A*1 = 87.50W | 87.50W - (-5W)87.5W*100 = 105.71% | 87.50W - (-15W)87.5W*100 = 117% |
| 3 | 20W + (-10W) = 10W | 3*10W = 30W | 3*120V*411x10-3A*1 = 85.42W | 85.42W - 10W85.42W*100 = 88.29% | 85.42W - 30W85.42W*100 = 64.88% |
| 4 | 25W + (-10W) = 15W | 3*15W = 45W | 3*120V*402*10-3A*1 = 85.55W | 85.55W -15 W85.55W*100 = 82.47% | 85.55W - 45 W85.55W*100 = 50.90% |

- During the balanced load test, it was assumed that the load and also the 3-phase voltage sources are balanced. In practice, they may not be ideally balanced. Describe how this may affect your measurement and/or calculation of power.

Unbalanced load test voltages and phase currents may be different when compared to the ideally balanced load test. This may result in the inaccurate measurement of power, and therefore resulting in varying calculations. As a result, there may also be errors in reactive power and power factor calculations, leading to an overestimation or underestimation of power values.

- Calculate the percentage of error for each method of power measurement assuming the corresponding calculation results as the base value.

Refer to Table 5 for percent errors.

- Using your measurement results in Table 4, calculate the total power delivered to the 3-phase load by using the 2-wattmeter and three-wattmeter methods and record your results in Table 6

Table 6 Comparison of Total 3-phase power for the unbalanced 3-phase load

| Two-Wattmeter Method | Three-Wattmeter Method | Summation of RI2’s In the Circuit. |
| --- | --- | --- |
| P1 = W1 + W2 | P2 = W3A + W3B + W3C |  |
| = 115W - 50W = 65W | 65W+65W+65W = 195W | 0*1.14A2+20*(504x10-3)2 + 40* (782x10-3)2 = 29.54W |

- Draw to scale the phasors of VAn, VBn, and VCn by using the measured phase voltages in section 3.4 for the unbalanced load. The voltage source is assumed to be balanced. Figure 4 shows a typical phasor diagram for an unbalanced three-phase star connected load.

- Measure V nN on your phasor diagram and compare it to the measured value in the actual circuit.

VnN, Measured = 2.17V

VnN = 0.045V

Conclusion

We gained a deeper understanding of various methods for measuring power in single-phase and three-phase systems. The two-wattmeter and three-wattmeter methods were employed to measure power in three-phase circuits under both balanced and unbalanced load conditions. A slight discrepancy was observed between theoretical and experimental values, likely due to the balanced load, which was expected to be perfectly balanced, but was not. This might have been due to the internal resistance in the wires while measurement, creating small differences in the measured power. This lab helped in our understanding of the three-phase power